{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["PosstionStringSheet","污染物超标报表","Sheet1"],"not_rendered":{"images":1,"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"PosstionStringSheet","index":0,"n_rows":1,"n_cols":1,"rows_kept":1,"hidden":true,"flags":["formulas_cached_only"]}
["污染物超标报表=0|1,1,2,8;1|3,1,128,8;&"]

{"sheet":"污染物超标报表","index":1,"n_rows":128,"n_cols":9,"rows_kept":128,"merged":[[0,0,0,7],[1,0,1,7]],"flags":["formulas_cached_only"]}
["污染物超标报表"]
["关注程度：国控.省控.市控  监控点类型：废水.废气  监测时间：2021-02-01至2021-02-28"]
["企业名称","监控点名称","超标污染物","报警值","报警开始时间","报警结束时间","超标上下限","超标倍数","超标原因"]
["安徽马钢表面技术股份有限公司","废水排口","化学需氧量(COD)",97.178,"2021-02-05 14:00:00","2021-02-05 15:00:00","0~80",0.2147]
["安徽马钢表面技术股份有限公司","废水排口","化学需氧量(COD)",82.2,"2021-02-26 10:00:00","2021-02-26 17:00:00","0~80",0.0275]
["安徽马钢表面技术股份有限公司","废水排口","化学需氧量(COD)",98.2,"2021-02-26 23:00:00","2021-02-27 01:00:00","0~80",0.2275]
["安徽马钢表面技术股份有限公司","超音速废水处理","化学需氧量(COD)",86.52,"2021-02-23 16:00:00","2021-02-23 23:00:00","0~80",0.0815]
["安徽马钢化工能源科技有限公司","化工能源北生化水处理排口","化学需氧量(COD)",110.662,"2021-02-01 15:00:00","2021-02-01 16:00:00","0~80",0.3833]
["安徽马钢化工能源科技有限公司","化工能源北生化水处理排口","化学需氧量(COD)",99.1,"2021-02-01 22:00:00","2021-02-02 00:00:00","0~80",0.2388]
["安徽马钢化工能源科技有限公司","化工能源北生化水处理排口","化学需氧量(COD)",84.832,"2021-02-14 15:00:00","2021-02-14 17:00:00","0~80",0.0604]
["山鹰国际控股股份公司","总排口","化学需氧量(COD)",119.952,"2021-02-25 14:00:00","2021-02-25 16:00:00","0~90",0.3328]
["马鞍山钢铁股份有限公司","炼焦南废水西排口","化学需氧量(COD)",828.825,"2021-02-07 23:00:00","2021-02-08 09:00:00","0~80",9.3603,"电磁阀漏液故障"]
["马鞍山钢铁股份有限公司","炼焦南废水西排口","化学需氧量(COD)",202.328,"2021-02-08 12:00:00","2021-02-08 17:00:00","0~80",1.5291,"电磁阀漏液故障"]
["马鞍山钢铁股份有限公司","炼铁南烧结废水排口","化学需氧量(COD)",117.914,"2021-02-07 22:00:00","2021-02-07 23:00:00","0~50",1.3583,"地面污水进入排口"]
["马鞍山钢铁股份有限公司","冷轧彩涂水处理排口","化学需氧量(COD)",129.351,"2021-02-09 22:00:00","2021-02-09 23:00:00","0~70",0.8479,"排口进入杂物干扰检测"]
["马鞍山钢铁股份有限公司","能控北2#排涝泵站","氨氮",6.68,"2021-02-24 11:00:00","2021-02-24 12:00:00","0~5",0.336,"水质波动"]
["马鞍山钢铁股份有限公司","能控北2#排涝泵站","氨氮",6.555,"2021-02-25 15:00:00","2021-02-25 18:00:00","0~5",0.311,"季度仪表比对"]
["马鞍山钢铁股份有限公司","能控北2#排涝泵站","氨氮",9.149,"2021-02-25 19:00:00","2021-02-25 22:00:00","0~5",0.8298,"季度仪表比对"]
["马鞍山钢铁股份有限公司","能控北2#排涝泵站","氨氮",11.707,"2021-02-26 18:00:00","2021-02-26 20:00:00","0~5",1.3414,"第四方核查"]
["马鞍山钢铁股份有限公司","能控北3#排涝泵站","化学需氧量(COD)",57.25,"2021-02-24 14:00:00","2021-02-24 15:00:00","0~50",0.145,"水质波动"]
["马鞍山钢铁股份有限公司","炼铁南铁区废水东排口","PH值",0,"2021-02-23 14:00:00","2021-02-23 15:00:00","6~9",7,"房所停电"]
["马鞍山钢铁股份有限公司","炼铁南铁区废水东排口","化学需氧量(COD)",184.2,"2021-02-01 02:00:00","2021-02-01 04:00:00","0~50",2.684,"下雨地面污水进入导致超标"]
["马鞍山钢铁股份有限公司","炼铁南铁区废水东排口","化学需氧量(COD)",141.828,"2021-02-01 14:00:00","2021-02-01 16:00:00","0~50",1.8366,"地面污水进入排口干扰检测"]
["马鞍山钢铁股份有限公司","炼铁南铁区废水东排口","化学需氧量(COD)",84.297,"2021-02-27 20:00:00","2021-02-27 21:00:00","0~50",0.6859,"下雨路面污水进入总排"]
["马鞍山钢铁股份有限公司","热电南总废水排口","PH值",2.451,"2021-02-08 22:00:00","2021-02-09 02:00:00","6~9",4.549,"废水中和系统故障 "]
["马鞍山钢铁股份有限公司","能控南二硅钢水处理排口","化学需氧量(COD)",75.767,"2021-02-25 13:00:00","2021-02-25 14:00:00","0~70",0.0824,"第四方核查"]
["马鞍山钢铁股份有限公司","冷轧北水处理排口","化学需氧量(COD)",207.9,"2021-02-09 18:00:00","2021-02-09 20:00:00","0~70",1.97,"管路结晶"]
["马鞍山钢铁股份有限公司","特钢废水总排","PH值",5.932,"2021-02-05 23:00:00","2021-02-06 00:00:00","6~9",1.068,"加酸系统故障"]
["马鞍山钢铁股份有限公司","特钢废水总排","化学需氧量(COD)",93.394,"2021-02-25 12:00:00","2021-02-25 13:00:00","0~50",0.8679,"第四方核查"]
["马鞍山钢铁股份有限公司","特钢废水总排","氨氮",5.191,"2021-02-05 22:00:00","2021-02-05 23:00:00","0~5",0.0382,"加酸系统故障"]
["马鞍山钢铁股份有限公司","特钢废水总排","氨氮",5.05,"2021-02-20 05:00:00","2021-02-20 06:00:00","0~5",0.01,"仪表反测"]
["马鞍山钢铁股份有限公司","特钢废水总排","氨氮",5.29,"2021-02-20 08:00:00","2021-02-20 12:00:00","0~5",0.058,"仪表反测"]
["马鞍山钢铁股份有限公司","能控南二硅钢铬处理","六价铬",0.517,"2021-02-25 12:00:00","2021-02-25 13:00:00","0~0.5",0.034,"第四方核查"]
["马鞍山钢铁股份有限公司","冷轧北含铬废水","六价铬",0.784,"2021-02-01 11:00:00","2021-02-01 12:00:00","0~0.5",0.568,"仪表反测"]
["马鞍山钢铁股份有限公司","轮轴废水排口","PH值",9.023,"2021-02-07 13:00:00","2021-02-07 14:00:00","6~9",1.0115]
["马鞍山钢铁股份有限公司","轮轴废水排口","PH值",9.014,"2021-02-09 16:00:00","2021-02-09 17:00:00","6~9",1.007]
["马鞍山钢铁股份有限公司","轮轴废水排口","化学需氧量(COD)",57.6,"2021-02-02 02:00:00","2021-02-02 04:00:00","0~50",0.152]
["马鞍山钢铁股份有限公司","轮轴废水排口","化学需氧量(COD)",56.5,"2021-02-03 10:00:00","2021-02-03 11:00:00","0~50",0.13]
["马鞍山钢铁股份有限公司","轮轴废水排口","化学需氧量(COD)",52.4,"2021-02-03 20:00:00","2021-02-03 21:00:00","0~50",0.048]
["马鞍山钢铁股份有限公司","轮轴废水排口","化学需氧量(COD)",52.856,"2021-02-05 08:00:00","2021-02-05 09:00:00","0~50",0.0571]
["马鞍山钢铁股份有限公司","轮轴废水排口","化学需氧量(COD)",57.153,"2021-02-09 11:00:00","2021-02-09 12:00:00","0~50",0.1431]
["马鞍山钢铁股份有限公司","轮轴废水排口","化学需氧量(COD)",52.2,"2021-02-23 18:00:00","2021-02-23 19:00:00","0~50",0.044]
["马鞍山钢铁股份有限公司","轮轴废水排口","化学需氧量(COD)",50.5,"2021-02-24 20:00:00","2021-02-24 21:00:00","0~50",0.01]
["马鞍山钢铁股份有限公司","长材北废水总排排口","化学需氧量(COD)",64.924,"2021-02-09 11:00:00","2021-02-09 12:00:00","0~50",0.2985,"排口进入杂物干扰检测"]
["马鞍山钢铁股份有限公司","长材北废水总排排口","化学需氧量(COD)",50.693,"2021-02-09 16:00:00","2021-02-09 19:00:00","0~50",0.0139,"排口进入杂物干扰检测"]
["马鞍山钢铁股份有限公司","长材北废水总排排口","化学需氧量(COD)",55.506,"2021-02-10 05:00:00","2021-02-10 06:00:00","0~50",0.1101,"水质波动"]
["马鞍山钢铁股份有限公司","长材北废水总排排口","化学需氧量(COD)",84.1,"2021-02-21 09:00:00","2021-02-21 10:00:00","0~50",0.682,"水质波动"]
["马鞍山钢铁股份有限公司","资源分公司回收二分厂排口","PH值",0,"2021-02-03 21:00:00","2021-02-03 22:00:00","6~9",7,"房所停电"]
["马鞍山钢铁股份有限公司","热电北废水排口","化学需氧量(COD)",53.9,"2021-02-05 16:00:00","2021-02-05 17:00:00","0~50",0.078,"雨水将地面污物冲入总渠"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",30.28,"2021-02-03 20:00:00","2021-02-03 21:00:00","0~30",0.0093,"生产工艺调整"]
["马鞍山钢铁股份有限公司","热电北11#炉排口","烟尘",5.49,"2021-02-04 16:00:00","2021-02-04 17:00:00","0~5",0.098,"因煤气品质差，排口烟尘超标。"]
["马鞍山钢铁股份有限公司","炼铁南1#烧结机混合烟道","二氧化硫",228.61,"2021-02-05 10:00:00","2021-02-05 11:00:00","0~180",0.2701,"检修启停机"]
["马鞍山澳新环保科技有限公司","焚烧炉","一氧化碳",1464.175,"2021-02-06 01:00:00","2021-02-06 07:00:00","0~80",17.3022]
["马鞍山钢铁股份有限公司","炼铁南1#烧结机混合烟道","二氧化硫",622.48,"2021-02-06 20:00:00","2021-02-06 22:00:00","0~180",2.4582,"脱硫脱硝增压风机工频运转，脱硫脱硝调整影响"]
["马鞍山钢铁股份有限公司","炼焦北7#8#焦炉出焦除尘","二氧化硫",30.12,"2021-02-13 19:00:00","2021-02-13 20:00:00","0~30",0.004,"CEMS工控机数据库出错"]
["马鞍山钢铁股份有限公司","炼铁南1#烧结机混合烟道","二氧化硫",525.63,"2021-02-15 21:00:00","2021-02-15 23:00:00","0~180",1.9202,"脱硫脱硝增压风机工频运转，脱硫脱硝调整影响"]
["马鞍山钢铁股份有限公司","炼铁南1#烧结机混合烟道","二氧化硫",542.46,"2021-02-04 21:00:00","2021-02-05 01:00:00","0~180",2.0137,"煤气波动，脱硫脱硝调整影响"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","氮氧化物",160.62,"2021-02-10 20:00:00","2021-02-10 21:00:00","0~150",0.0708,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦南3#4#焦炉排口","氮氧化物",150.011,"2021-02-16 01:00:00","2021-02-16 02:00:00","0~150",0.0001,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",31.25,"2021-02-18 15:00:00","2021-02-18 16:00:00","0~30",0.0417,"生产调整"]
["马鞍山钢铁股份有限公司","炼铁南2#炉炉前除尘","烟尘",15.17,"2021-02-18 17:00:00","2021-02-18 19:00:00","0~15",0.0113,"除尘器脉冲阀故障"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",32.89,"2021-02-19 00:00:00","2021-02-19 04:00:00","0~30",0.0963,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",35.78,"2021-02-19 09:00:00","2021-02-19 10:00:00","0~30",0.1927,"生产调整"]
["马鞍山澳新环保科技有限公司","焚烧炉","一氧化碳",129.827,"2021-02-20 01:00:00","2021-02-20 02:00:00","0~80",0.6228]
["马鞍山钢铁股份有限公司","炼焦北7#8#焦炉出焦除尘","二氧化硫",30.27,"2021-02-20 18:00:00","2021-02-20 19:00:00","0~30",0.009,"生产调整"]
["光大江东环保能源（马鞍山）有限公司","3#炉","烟尘",30.135,"2021-02-01 08:00:00","2021-03-13 20:00:00","0~30",0.0045]
["马鞍山钢铁股份有限公司","炼焦南1#2#干熄焦除尘","烟尘",43.87,"2021-02-02 10:00:00","2021-02-02 11:00:00","0~30",0.4623,"仪表比对"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",37.75,"2021-02-02 19:00:00","2021-02-02 20:00:00","0~30",0.2583,"检测仪表故障"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",31.57,"2021-02-02 21:00:00","2021-02-02 22:00:00","0~30",0.0523,"检测仪表故障"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",32.81,"2021-02-03 10:00:00","2021-02-03 11:00:00","0~30",0.0937,"反吹气源中断"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",31.11,"2021-02-03 15:00:00","2021-02-03 16:00:00","0~30",0.037,"反吹气源中断"]
["马鞍山钢铁股份有限公司","炼焦北7#8#焦炉出焦除尘","二氧化硫",30.76,"2021-02-03 16:00:00","2021-02-03 17:00:00","0~30",0.0253,"平台数据维护"]
["马鞍山钢铁股份有限公司","炼铁南1#2#竖炉脱硫排口","二氧化硫",250.29,"2021-02-03 17:00:00","2021-02-03 18:00:00","0~180",0.3905,"雾化器故障更换脱硫效果差"]
["马鞍山钢铁股份有限公司","炼铁南1#烧结机混合烟道","二氧化硫",265.83,"2021-02-05 05:00:00","2021-02-05 08:00:00","0~180",0.4768,"检修启停机"]
["马鞍山钢铁股份有限公司","炼铁南1#烧结机混合烟道","二氧化硫",184.16,"2021-02-07 02:00:00","2021-02-07 06:00:00","0~180",0.0231,"脱硫脱硝增压风机工频运转，脱硫脱硝调整影响"]
["马鞍山钢铁股份有限公司","炼铁南2#烧结机排口","氮氧化物",386.4,"2021-02-08 10:00:00","2021-02-08 11:00:00","0~300",0.288,"仪表比对"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","氮氧化物",151.71,"2021-02-09 19:00:00","2021-02-09 20:00:00","0~150",0.0114,"仪表故障，氮氧化物数值飘移。"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",31.33,"2021-02-09 23:00:00","2021-02-10 00:00:00","0~30",0.0443,"生产调整"]
["山鹰国际控股股份公司","7号炉","二氧化硫",67.391,"2021-02-04 08:00:00","2021-02-04 09:00:00","0~50",0.3478]
["马鞍山钢铁股份有限公司","炼铁南1#烧结机混合烟道","二氧化硫",183.83,"2021-02-08 04:00:00","2021-02-08 05:00:00","0~180",0.0213,"脱硫脱硝增压风机工频运转，脱硫脱硝调整影响"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",33.39,"2021-02-10 06:00:00","2021-02-10 07:00:00","0~30",0.113,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦北7#8#焦炉出焦除尘","二氧化硫",31.59,"2021-02-10 10:00:00","2021-02-10 11:00:00","0~30",0.053,"仪表标定"]
["马鞍山钢铁股份有限公司","炼焦南3#4#焦炉出焦除尘","二氧化硫",30.02,"2021-02-10 10:00:00","2021-02-10 11:00:00","0~30",0.0007,"标定"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",30.22,"2021-02-10 11:00:00","2021-02-10 12:00:00","0~30",0.0073,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦南3#干熄焦环境除尘","烟尘",39.1017,"2021-02-10 14:00:00","2021-02-10 15:00:00","0~30",0.3034,"仪表故障"]
["马鞍山钢铁股份有限公司","炼焦南3#干熄焦环境除尘","二氧化硫",87.2208,"2021-02-11 00:00:00","2021-02-11 01:00:00","0~80",0.0903,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦南5#6#焦炉出焦除尘","二氧化硫",37.31,"2021-02-11 10:00:00","2021-02-11 11:00:00","0~30",0.2437,"标定"]
["马鞍山钢铁股份有限公司","炼铁南2#炉顶吸除尘","烟尘",16.15,"2021-02-11 15:00:00","2021-02-11 16:00:00","0~15",0.0767,"仪表比对"]
["马鞍山钢铁股份有限公司","炼焦北4#5#干熄焦除尘","二氧化硫",270.37,"2021-02-13 04:00:00","2021-02-13 05:00:00","0~80",2.3796,"生产调整"]
["山鹰国际控股股份公司","9号炉","烟尘",13.712,"2021-02-04 04:00:00","2021-02-04 05:00:00","0~10",0.3712,"生产调整"]
["山鹰国际控股股份公司","7号炉","氮氧化物",380.178,"2021-02-06 17:00:00","2021-02-06 18:00:00","0~100",2.8018,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",33.51,"2021-02-10 23:00:00","2021-02-11 00:00:00","0~30",0.117,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦南3#干熄焦环境除尘","二氧化硫",92.5981,"2021-02-11 16:00:00","2021-02-11 18:00:00","0~80",0.1575,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦北4#5#干熄焦除尘","二氧化硫",186.66,"2021-02-13 06:00:00","2021-02-13 08:00:00","0~80",1.3333,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",30.25,"2021-02-21 13:00:00","2021-02-21 14:00:00","0~30",0.0083,"反吹气源切断影响 "]
["马鞍山钢铁股份有限公司","炼焦北6#干熄焦除尘","烟尘",33.15,"2021-02-22 19:00:00","2021-02-22 20:00:00","0~30",0.105,"粉尘仪光学镜片污染"]
["马鞍山钢铁股份有限公司","炼铁北B烧结机尾排口","烟尘",47.73,"2021-02-24 04:00:00","2021-02-24 05:00:00","0~20",1.3865,"检修启停机"]
["马鞍山钢铁股份有限公司","炼焦南3#4#焦炉出焦除尘","二氧化硫",36.19,"2021-02-24 10:00:00","2021-02-24 11:00:00","0~30",0.2063,"标定"]
["马鞍山钢铁股份有限公司","炼铁南1#烧结机混合烟道","二氧化硫",492.42,"2021-02-17 20:00:00","2021-02-17 22:00:00","0~180",1.7357,"脱硝直燃炉点火"]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",30.75,"2021-02-20 10:00:00","2021-02-20 11:00:00","0~30",0.025,"仪表比对"]
["马鞍山钢铁股份有限公司","炼铁北B烧结脱硫脱硝排口","二氧化硫",188.193,"2021-02-24 18:00:00","2021-02-24 21:00:00","0~180",0.0455,"检修启停机"]
["马鞍山钢铁股份有限公司","炼焦南5#6#焦炉出焦除尘","二氧化硫",42.26,"2021-02-25 10:00:00","2021-02-25 11:00:00","0~30",0.4087,"仪表比对"]
["马鞍山钢铁股份有限公司","炼焦南5#6#焦炉出焦除尘","烟尘",32.81,"2021-02-25 10:00:00","2021-02-25 11:00:00","0~30",0.0937,"仪表比对"]
["马鞍山钢铁股份有限公司","炼铁南1#烧结机混合烟道","烟尘",63,"2021-02-25 18:00:00","2021-02-25 19:00:00","0~40",0.575,"检修启停机"]
["马鞍山澳新环保科技有限公司","焚烧炉","一氧化碳",87.547,"2021-02-25 22:00:00","2021-02-25 23:00:00","0~80",0.0943]
["马鞍山澳新环保科技有限公司","焚烧炉","一氧化碳",396.447,"2021-02-26 01:00:00","2021-02-26 03:00:00","0~80",3.9556]
["马鞍山澳新环保科技有限公司","焚烧炉","烟尘",88.969,"2021-02-26 01:00:00","2021-02-26 02:00:00","0~80",0.1121]
["马鞍山钢铁股份有限公司","炼铁南1#烧结机混合烟道","二氧化硫",209.96,"2021-02-07 08:00:00","2021-02-07 09:00:00","0~180",0.1664,"脱硫脱硝增压风机工频运转，脱硫脱硝调整影响"]
["光大江东环保能源（马鞍山）有限公司","3#炉","二氧化硫",298.649,"2021-02-11 00:00:00","2021-03-01 00:00:00","0~100",1.9865]
["安徽马钢化工能源科技有限公司","硫铵除尘","烟尘",51.66,"2021-02-20 23:00:00","2021-02-21 01:00:00","0~50",0.0332]
["马鞍山钢铁股份有限公司","热电南6#炉排口","氮氧化物",108.758,"2021-02-26 18:00:00","2021-02-26 21:00:00","0~100",0.0876,"停炉"]
["马鞍山钢铁股份有限公司","炼铁南2#炉顶吸除尘","烟尘",19.62,"2021-02-27 15:00:00","2021-02-27 16:00:00","0~15",0.308,"仪表比对"]
["马鞍山澳新环保科技有限公司","焚烧炉","一氧化碳",83.129,"2021-02-28 11:00:00","2021-02-28 13:00:00","0~80",0.0391]
["山鹰国际控股股份公司","7号炉","氮氧化物",134.12,"2021-02-07 06:00:00","2021-02-07 09:00:00","0~100",0.3412]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","二氧化硫",36.39,"2021-02-10 15:00:00","2021-02-10 17:00:00","0~30",0.213,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦北8#焦炉脱硫脱硝排口","二氧化硫",36.46,"2021-02-20 08:00:00","2021-02-20 09:00:00","0~30",0.2153,"仪表比对"]
["马鞍山钢铁股份有限公司","炼铁北B烧结机尾排口","烟尘",49.65,"2021-02-23 20:00:00","2021-02-23 22:00:00","0~20",1.4825,"检修启停机"]
["马鞍山钢铁股份有限公司","炼焦南6#焦炉排口","氮氧化物",153.824,"2021-02-25 09:00:00","2021-02-25 10:00:00","0~150",0.0255,"仪表比对"]
["马鞍山钢铁股份有限公司","热电南6#炉排口","烟尘",31.032,"2021-02-26 16:00:00","2021-02-26 21:00:00","0~10",2.1032,"停炉"]
["安徽马鞍山万能达发电有限责任公司","4号机组废气排放口","烟尘",65.209,"2021-03-04 21:00:00","/","0~20",2.2605]
["马鞍山钢铁股份有限公司","炼焦南3#干熄焦环境除尘","二氧化硫",84.6175,"2021-02-12 19:00:00","2021-02-12 20:00:00","0~80",0.0577,"生产调整"]
["马鞍山钢铁股份有限公司","炼焦南1#2#干熄焦除尘","二氧化硫",99.67,"2021-02-23 10:00:00","2021-02-23 11:00:00","0~80",0.2459,"标定值异常上传"]
["马鞍山澳新环保科技有限公司","焚烧炉","一氧化碳",140.746,"2021-02-25 19:00:00","2021-02-25 20:00:00","0~80",0.7593]
["马鞍山钢铁股份有限公司","热电南6#炉排口","二氧化硫",45.506,"2021-02-26 18:00:00","2021-02-26 21:00:00","0~35",0.3002,"停炉"]
["马鞍山澳新环保科技有限公司","焚烧炉","一氧化碳",273.677,"2021-02-26 04:00:00","2021-02-26 07:00:00","0~80",2.421]
["马鞍山钢铁股份有限公司","炼焦南5#焦炉排口","氮氧化物",162.1,"2021-02-20 10:00:00","2021-02-20 11:00:00","0~150",0.0807,"仪表比对"]
["马鞍山钢铁股份有限公司","炼焦北6#干熄焦除尘","烟尘",31.46,"2021-02-22 11:00:00","2021-02-22 12:00:00","0~30",0.0487,"市局进行人工采样比对"]
["马鞍山钢铁股份有限公司","热电南6#炉排口","二氧化硫",35.876,"2021-02-26 22:00:00","2021-02-26 23:00:00","0~35",0.025,"停炉"]

{"sheet":"Sheet1","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"hidden":true,"flags":["formulas_cached_only"]}